# Buildings Department

# Practice Note for Authorized Persons

and Registered Structural Engineers

201

## Access Facilities for Telecommunications and Broadcasting Services

Introduction

The world is undergoing a technological revolution and entering the Information Age.  Hong Kong is well placed to reap the benefits and maintain our competitive edge in this new era.  The Government's policy objective is to develop Hong Kong into a telecommunications, broadcasting and Internet hub.

2.	Consumers should be able to enjoy quality broadcasting, telecommunications and Internet services at their choice.  To enable occupiers of a building to have access to the full range of such services, and to enable all telecommunications and broadcasting network operators to have access to customers in buildings on a non-discriminatory basis to ensure fair competition, the Telecommunications Authority has, under section 14 of the Telecommunication Ordinance, granted authorization to fixed telecommunications network operators and a subscription television broadcasting network operator to place and maintain telecommunication line in the common parts of buildings in private ownership.  New telecommunications network operators and broadcast operators may be licensed from time to time to provide new telecommunications and broadcasting services.

3.	To enable the networks operators to accommodate their equipment and wiring in buildings, Regulation 28A of the Building (Planning) Regulations have been enacted and will come in operation on 1 November 2000, requiring every commercial building, industrial building, residential building (other than a building for residence of a single family) and hotel building to be provided with access facilities for telecommunication and broadcasting services in accordance with the design requirements specified by the Building Authority (BA).

4.	This practice note specifies the BA's requirements on the design of such facilities.

Facilities for Telecommunications and Broadcasting Services

5.	The minimum number and size of lead-in duct, telecommunication and

/broadcasting …..

- 2 -

broadcasting (TBE) rooms and vertical riser slots shall be provided in accordance with the requirements specified in Appendix A.

6.	The TBE room should be placed at a location not susceptible to flooding.  For development with mixed uses comprising separate tower blocks on top of a commercial podium, separate TBE rooms should be provided within each tower block and the commercial podium to serve each zone.

7.	In addition, the TBE room should also comply with the following requirements :-

(i)	the room should be linked up with the vertical block wiring system of the buildings

(ii)	no water pipes, sewage pipes, water drainage, water sprinklers, high voltage power supply (exceeding 600V between phase and earth for three-phase, or 1000V for single-phase, or 1500V dc) cables, power transformers should be installed within the TBE rooms;

(iii)	sufficient lighting, electricity supply and ventilation should be provided;

(iv)	separate telecommunications earth electrode should be provided; and

(v)	minimum clear height of 2.8 metres should be provided.

8.		A schematic arrangement of the access facilities is attached at Appendix B for general reference.

(C M LEUNG)

Building Authority

Ref. : BD GP/BREG/P/37

First issue November 1997

This revision September 2000 (AD/NB1) – Generally revamped

Index under : Access Facilities for Telecommunications and Broadcasting Services

Appendix A

PNAP 201

Requirements of Access Facilities for Telecommunications and Broadcasting Services

| OFFICE/COMMERCIAL, INDUSTRIAL BUILDINGS AND SHOPPING ARCADES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Usable floor area, Æ ( 1000 m2) | Æ  2 | 2 <Æ  4 | 4 < Æ  12 | 12 < Æ  24 | 24 < Æ  48 | 48 < Æ  72 | 72 < Æ  96 | 96 < Æ  120 | 120 < Æ  144 |
| No. of lead-in duct Inside diameter of lead-in duct (mm) | 2 100 | 3 100 | 3 100 | 4 100 | 4 100 | 8 100 | 8 100 | 8 100 | 8 100 |
| Minimum Area of TBE Room (m2) Clear Height of TBE Room (m) | Not Required | 22 3 | 42 3 | 51 3 | 61 3 | 79 3 | 88 3 | 107 3 | 113 3 |
| Vertical riser (mm) No. of vertical riser slot | 100  100 2 | 300  200 2 | 300  200 2 | 400  200 2 | 400  200 2 | 600  250 2 | 650  250 2 | 750  250 2 | 900  250 2 |

| RESIDENTIAL BUILDINGS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of flats in a block, N | N  5 | 5 < N  50 | 50 < N  100 | 100 < N  250 | 250 < N  500 | 500 < N  750 | 750 < N  1000 | 1000 < N  1500 |  |  |
| No. of lead-in duct Inside diameter of lead-in duct (mm) | 2 100 | 3 100 | 3 100 | 3 100 | 4 100 | 4 100 | 4 100 | 4 100 |  |  |
| Minimum Area of TBE Room (m2) Clear Height of TBE Room (m) | Not Required | 7 2.8 | 21 2.8 | 24 2.8 | 29 2.8 | 39 2.8 | 43 3 | 48 3 |  |  |
| Vertical riser (mm) No. of vertical riser slot | 75  75 1 | 200  100 1 | 200  100 1 | 200  200 1 | 300  200 1 | 300  200 2 | 300  200 2 | 400  200 2 |  |  |

| HOTELS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| No. of rooms, N | N  200 | 200 < N  400 | 400 < N  600 | 600 < N  800 | 800 < N  1000 | 1000 < N  1200 |
| No. of lead-in duct Inside diameter of lead-in duct (mm) | 3 100 | 3 100 | 3 100 | 3 100 | 3 100 | 3 100 |
| Minimum Area of TBE Room (m2) Clear Height of TBE Room (m) | 24 3 | 24 3 | 26 3 | 28 3 | 35 3 | 37 3 |
| Vertical riser (mm) No. of vertical riser slot | 200  200 1 | 300  200 1 | 300  200 2 | 300  200 2 | 400  200 2 | 400  200 2 |

Note 1 : The definition of " Usable Floor Area" shall have the same meaning as defined in the Building (Planning) Regulations.