Buildings Department

Practice Note for Authorized Persons

and Registered Structural Engineers

230

Water Seepage

Water seepage has been a cause for concern to a number of Government departments including the Buildings Department.  Causes of seepage are many and varied but one of the common sources of seepage relates to water-borne piping embedded in the structural members of a building.

2.		The problems associated with water seepage of the above-mentioned nature is complex and difficult to resolve for the following reasons :

(i)	The party affected (lower floor) is normally not the one who created the problem (upper floor), therefore co-operation is usually not forthcoming.  If common areas are involved, multiple ownership status of such areas further complicates the problem;

(ii)	It is difficult to locate the defective sections of water-borne piping for repair, as water leaks and finds its path of least resistance through cracks and ducts; and

(iii)	Even if such defective sections are accurately identified, the breaking up of structural elements for repair is very costly and disruptive to the occupiers, which would discourage them from co-operating.

3.		Water seepage arising from embedded piping causes not only nuisance but also deterioration to the structural member of a building if unattended for a prolonged period.  This practice note seeks your co-operation to cure the problem at source.  You are strongly advised to design the routing of all water-borne piping off structural elements to facilitate the indispensable need for repair and replacement of such piping during the design life of the building, which would normally outlast the design life of the piping.  The huge benefit to the consumers and the public that this will bring about in terms of easy maintenance of the building for its entire design life will certainly outweigh the efforts you, as Authorized Persons and Registered Structural Engineers, have to make at the design stage of a building project.

- To ensure the long-term integrity of all structural elements and also to avoid sanitary nuisance arising from water seepage, you are required to state explicitly in the drainage plans that no water-borne piping, other than that specified in paragraph 2 of the guidelines at Appendix A, will be embedded in structural elements.  If despite my advice you still decide to embed any section of such piping in any structural elements, you will be required to submit for my consideration details showing the routing of all

/ water-borne .....

- 2 -

water-borne pipes when you apply for approval of drainage plans and to justify to my entire satisfaction  how  you  would  achieve  the  above  objective of ensuring the long-term integrity of such structural elements.  Omission of such routing details, or the justification of such omission as the case may be, would result in disapproval of plans under Section 16(1)(i) of the Buildings Ordinance.  This will take immediate effect for all new building projects for which building plans are submitted for the first time for approval.

5.		Your attention is also drawn to the importance of preventing water seepage from other sources, particularly the following :

- inadequate water-proofing construction and design of floor and roof slabs;

- poor workmanship in laying and fixing water-borne piping;

- sub-standard sanitary fitments; and

- lack of attention to ponding of water, eg. underneath bath tubs and washing machines.

6.		To assist designers to route water borne pipes off structural elements, the Building Authority is prepared to grant modification to permit genuine and properly designed pipes ducts which are provided with adequate access for inspection and maintenance in new buildings to be excluded from gross floor area calculation.

( C M LEUNG )

Building Authority

Ref. :  GP/BORD/92

GP/BREG/P/9 (III)

First issue October 1999

This revision March 2000 (AD/D) (para. 3(d) of Appendix A and para. 6 added)

Index under :	Water seepage

Water-borne piping embedded in structural elements

Appendix A

PNAP 230

# Guidelines on embedment of water-borne pipes

1.	In general, embedment of water-borne pipes in structural members, other than those specified in paragraph 2, would not be permitted within columns, slabs, structural walls, beams or transfer plates.

2.	Water-borne pipes piercing through the following structural members may be permitted where it is demonstrated that no adverse effect will be caused to the performance of the structural members and, where the pipes are easily accessible for maintenance :

(a)	Vertical pipes piercing through structural slabs, transfer plates; and

(b)	Horizontal pipes piercing through beams, columns or structural walls.

3.	In the context of para. 2, no adverse effect may be assumed in the following circumstances :

(a)	Vertical pipes piercing through r.c. floor slabs, transfer plates :-

(i)	The size of a hole formed is not greater than 150mm in diameter and no main reinforcement is severed to make way for the hole;

(ii)	Trimming bars not less than the size of the main reinforcement of the slab are provided around the hole.

(b)	Horizontal pipes piercing through r.c. beams :-

(i)	The size of a hole formed is not greater than 150mm in diameter or 1/3 the depth of the beam, whichever is the less;

(ii)	The hole is formed at the neutral axis of the beam section; and

(iii)	Vertical and horizontal trimming bars not less than 16mm in diameter are provided around the hole and at each side of the beam.

(c)	Horizontal pipes piercing through structural walls :-

(i)	The size of a hole formed is not greater than 150mm in diameter or the minimum bar spacing of the vertical reinforcement of the wall, whichever is the less; and

(ii)	Vertical and horizontal trimming bars of size of not less than the vertical reinforcement bars of the wall are provided around the hole and at both side of the wall.

(d)	Embedment of drainage pipes for disposal of condensation from air-conditioning units.

Ref.: BD GP/BORD/92

First issue October 1999

This revision March 2000